## Overview
Aqua Rig alarm review | Aqua Rig alarm review | Aqua Rig alarm review | Aqua Rig alarm review | Aqua Rig alarm review | Aqua Rig alarm review | Aqua Rig alarm review | Aqua Rig alarm review
AR-V1-01-RE26 / 23 October 2026 | AR-V1-01-RE26 / 23 October 2026 | AR-V1-01-RE26 / 23 October 2026 | AR-V1-01-RE26 / 23 October 2026 | AR-V1-01-RE26 / 23 October 2026 | AR-V1-01-RE26 / 23 October 2026 | AR-V1-01-RE26 / 23 October 2026 | AR-V1-01-RE26 / 23 October 2026
LISTED TAGS | LISTED TAGS | PROPOSED NOTIFY | PROPOSED NOTIFY | PROPOSED NO NOTIFY | PROPOSED NO NOTIFY | HMI ENABLED | HMI ENABLED
109 |  | 44 |  | 65 |  | 44
Configuration basis | Configuration basis | Configuration basis | Configuration basis | Configuration basis | Configuration basis | Configuration basis | Configuration basis
Site / module | Site / module | AR-V1-01-RE26 - Aqua Rig | AR-V1-01-RE26 - Aqua Rig | AR-V1-01-RE26 - Aqua Rig | AR-V1-01-RE26 - Aqua Rig | AR-V1-01-RE26 - Aqua Rig | AR-V1-01-RE26 - Aqua Rig
Scope | Scope | 89 Boolean alarms and 20 diagnostic companions. All 109 GVL variables are listed. | 89 Boolean alarms and 20 diagnostic companions. All 109 GVL variables are listed. | 89 Boolean alarms and 20 diagnostic companions. All 109 GVL variables are listed. | 89 Boolean alarms and 20 diagnostic companions. All 109 GVL variables are listed. | 89 Boolean alarms and 20 diagnostic companions. All 109 GVL variables are listed. | 89 Boolean alarms and 20 diagnostic companions. All 109 GVL variables are listed.
HMI source | HMI source | Latest AquaRig_Alarms_Import.xml, including the agreed PT123, PT191 and VFD adjustments. | Latest AquaRig_Alarms_Import.xml, including the agreed PT123, PT191 and VFD adjustments. | Latest AquaRig_Alarms_Import.xml, including the agreed PT123, PT191 and VFD adjustments. | Latest AquaRig_Alarms_Import.xml, including the agreed PT123, PT191 and VFD adjustments. | Latest AquaRig_Alarms_Import.xml, including the agreed PT123, PT191 and VFD adjustments. | Latest AquaRig_Alarms_Import.xml, including the agreed PT123, PT191 and VFD adjustments.
Notify proposal | Notify proposal | Boolean alarm Notify follows HMI Enabled as a proposal only. Diagnostic fields are proposed FALSE. | Boolean alarm Notify follows HMI Enabled as a proposal only. Diagnostic fields are proposed FALSE. | Boolean alarm Notify follows HMI Enabled as a proposal only. Diagnostic fields are proposed FALSE. | Boolean alarm Notify follows HMI Enabled as a proposal only. Diagnostic fields are proposed FALSE. | Boolean alarm Notify follows HMI Enabled as a proposal only. Diagnostic fields are proposed FALSE. | Boolean alarm Notify follows HMI Enabled as a proposal only. Diagnostic fields are proposed FALSE.
JSON status | JSON status | No Aqua Rig notification JSON was supplied. Routing and Type values require confirmation before JSON generation. | No Aqua Rig notification JSON was supplied. Routing and Type values require confirmation before JSON generation. | No Aqua Rig notification JSON was supplied. Routing and Type values require confirmation before JSON generation. | No Aqua Rig notification JSON was supplied. Routing and Type values require confirmation before JSON generation. | No Aqua Rig notification JSON was supplied. Routing and Type values require confirmation before JSON generation. | No Aqua Rig notification JSON was supplied. Routing and Type values require confirmation before JSON generation.
Description | Description | Boolean alarm descriptions are copied from the current HMI XML. [!tag] references preserve the captured value. | Boolean alarm descriptions are copied from the current HMI XML. [!tag] references preserve the captured value. | Boolean alarm descriptions are copied from the current HMI XML. [!tag] references preserve the captured value. | Boolean alarm descriptions are copied from the current HMI XML. [!tag] references preserve the captured value. | Boolean alarm descriptions are copied from the current HMI XML. [!tag] references preserve the captured value. | Boolean alarm descriptions are copied from the current HMI XML. [!tag] references preserve the captured value.
Notify editing | Notify editing | TRUE/FALSE are native Boolean values. In Excel, use Insert > Checkbox if desired. Blank means undecided. | TRUE/FALSE are native Boolean values. In Excel, use Insert > Checkbox if desired. Blank means undecided. | TRUE/FALSE are native Boolean values. In Excel, use Insert > Checkbox if desired. Blank means undecided. | TRUE/FALSE are native Boolean values. In Excel, use Insert > Checkbox if desired. Blank means undecided. | TRUE/FALSE are native Boolean values. In Excel, use Insert > Checkbox if desired. Blank means undecided. | TRUE/FALSE are native Boolean values. In Excel, use Insert > Checkbox if desired. Blank means undecided.
Agreed alarm behaviour | Agreed alarm behaviour | Agreed alarm behaviour | Agreed alarm behaviour | Agreed alarm behaviour | Agreed alarm behaviour | Agreed alarm behaviour | Agreed alarm behaviour
PT122 / PT123 | PT122 / PT123 | Only YF and WH enabled for both pressure transmitters. | Only YF and WH enabled for both pressure transmitters. | Only YF and WH enabled for both pressure transmitters. | Only YF and WH enabled for both pressure transmitters. | Only YF and WH enabled for both pressure transmitters. | Only YF and WH enabled for both pressure transmitters.
PT191 | PT191 | Only YF enabled. All pressure limits and warnings disabled. | Only YF enabled. All pressure limits and warnings disabled. | Only YF enabled. All pressure limits and warnings disabled. | Only YF enabled. All pressure limits and warnings disabled. | Only YF enabled. All pressure limits and warnings disabled. | Only YF enabled. All pressure limits and warnings disabled.
VFD feedback | VFD feedback | VFD101 / 111 / 121 / 122: only YF enabled. AHH / WH / WL / ALL disabled. | VFD101 / 111 / 121 / 122: only YF enabled. AHH / WH / WL / ALL disabled. | VFD101 / 111 / 121 / 122: only YF enabled. AHH / WH / WL / ALL disabled. | VFD101 / 111 / 121 / 122: only YF enabled. AHH / WH / WL / ALL disabled. | VFD101 / 111 / 121 / 122: only YF enabled. AHH / WH / WL / ALL disabled. | VFD101 / 111 / 121 / 122: only YF enabled. AHH / WH / WL / ALL disabled.
VFD digital fault | VFD digital fault | All four VFD F_Y signals disabled; faults represented by the SBE alarms. | All four VFD F_Y signals disabled; faults represented by the SBE alarms. | All four VFD F_Y signals disabled; faults represented by the SBE alarms. | All four VFD F_Y signals disabled; faults represented by the SBE alarms. | All four VFD F_Y signals disabled; faults represented by the SBE alarms. | All four VFD F_Y signals disabled; faults represented by the SBE alarms.
Presentation | Presentation | No Machine 1 text in descriptions. Every _YF description includes Fault. | No Machine 1 text in descriptions. Every _YF description includes Fault. | No Machine 1 text in descriptions. Every _YF description includes Fault. | No Machine 1 text in descriptions. Every _YF description includes Fault. | No Machine 1 text in descriptions. Every _YF description includes Fault. | No Machine 1 text in descriptions. Every _YF description includes Fault.
Review before notification JSON is generated | Review before notification JSON is generated | Review before notification JSON is generated | Review before notification JSON is generated | Review before notification JSON is generated | Review before notification JSON is generated | Review before notification JSON is generated | Review before notification JSON is generated
Confirm the proposed Notify values independently of HMI Enabled, including TestAlarm. | Confirm the proposed Notify values independently of HMI Enabled, including TestAlarm. | Confirm the proposed Notify values independently of HMI Enabled, including TestAlarm. | Confirm the proposed Notify values independently of HMI Enabled, including TestAlarm. | Confirm the proposed Notify values independently of HMI Enabled, including TestAlarm. | Confirm the proposed Notify values independently of HMI Enabled, including TestAlarm. | Confirm the proposed Notify values independently of HMI Enabled, including TestAlarm. | Confirm the proposed Notify values independently of HMI Enabled, including TestAlarm.
Confirm Type categories for new SBE / OA alarms. Current categories follow the HMI groups. | Confirm Type categories for new SBE / OA alarms. Current categories follow the HMI groups. | Confirm Type categories for new SBE / OA alarms. Current categories follow the HMI groups. | Confirm Type categories for new SBE / OA alarms. Current categories follow the HMI groups. | Confirm Type categories for new SBE / OA alarms. Current categories follow the HMI groups. | Confirm Type categories for new SBE / OA alarms. Current categories follow the HMI groups. | Confirm Type categories for new SBE / OA alarms. Current categories follow the HMI groups. | Confirm Type categories for new SBE / OA alarms. Current categories follow the HMI groups.
Confirm diagnostic routing. YFI codes and YFS / FaultStatus strings are proposed no_notify. | Confirm diagnostic routing. YFI codes and YFS / FaultStatus strings are proposed no_notify. | Confirm diagnostic routing. YFI codes and YFS / FaultStatus strings are proposed no_notify. | Confirm diagnostic routing. YFI codes and YFS / FaultStatus strings are proposed no_notify. | Confirm diagnostic routing. YFI codes and YFS / FaultStatus strings are proposed no_notify. | Confirm diagnostic routing. YFI codes and YFS / FaultStatus strings are proposed no_notify. | Confirm diagnostic routing. YFI codes and YFS / FaultStatus strings are proposed no_notify. | Confirm diagnostic routing. YFI codes and YFS / FaultStatus strings are proposed no_notify.
Check valve string lengths: GVL declares STRING(40), while the data model exports string-81. | Check valve string lengths: GVL declares STRING(40), while the data model exports string-81. | Check valve string lengths: GVL declares STRING(40), while the data model exports string-81. | Check valve string lengths: GVL declares STRING(40), while the data model exports string-81. | Check valve string lengths: GVL declares STRING(40), while the data model exports string-81. | Check valve string lengths: GVL declares STRING(40), while the data model exports string-81. | Check valve string lengths: GVL declares STRING(40), while the data model exports string-81. | Check valve string lengths: GVL declares STRING(40), while the data model exports string-81.
Sources | Sources | Sources | Sources | Sources | Sources | Sources | Sources
Alarm content: AquaRig_Alarms_Import.xml (latest agreed revision in this chat). | Alarm content: AquaRig_Alarms_Import.xml (latest agreed revision in this chat). | Alarm content: AquaRig_Alarms_Import.xml (latest agreed revision in this chat). | Alarm content: AquaRig_Alarms_Import.xml (latest agreed revision in this chat). | Alarm content: AquaRig_Alarms_Import.xml (latest agreed revision in this chat). | Alarm content: AquaRig_Alarms_Import.xml (latest agreed revision in this chat). | Alarm content: AquaRig_Alarms_Import.xml (latest agreed revision in this chat). | Alarm content: AquaRig_Alarms_Import.xml (latest agreed revision in this chat).
Names / types: supplied Aqua Rig Alarms GVL and OPCUA Client_dataModel.xml. | Names / types: supplied Aqua Rig Alarms GVL and OPCUA Client_dataModel.xml. | Names / types: supplied Aqua Rig Alarms GVL and OPCUA Client_dataModel.xml. | Names / types: supplied Aqua Rig Alarms GVL and OPCUA Client_dataModel.xml. | Names / types: supplied Aqua Rig Alarms GVL and OPCUA Client_dataModel.xml. | Names / types: supplied Aqua Rig Alarms GVL and OPCUA Client_dataModel.xml. | Names / types: supplied Aqua Rig Alarms GVL and OPCUA Client_dataModel.xml. | Names / types: supplied Aqua Rig Alarms GVL and OPCUA Client_dataModel.xml.
Workbook structure: Kristiansand Alarm JSON Review v3. Style: Renasys Ignition presentation, 8 October 2026. | Workbook structure: Kristiansand Alarm JSON Review v3. Style: Renasys Ignition presentation, 8 October 2026. | Workbook structure: Kristiansand Alarm JSON Review v3. Style: Renasys Ignition presentation, 8 October 2026. | Workbook structure: Kristiansand Alarm JSON Review v3. Style: Renasys Ignition presentation, 8 October 2026. | Workbook structure: Kristiansand Alarm JSON Review v3. Style: Renasys Ignition presentation, 8 October 2026. | Workbook structure: Kristiansand Alarm JSON Review v3. Style: Renasys Ignition presentation, 8 October 2026. | Workbook structure: Kristiansand Alarm JSON Review v3. Style: Renasys Ignition presentation, 8 October 2026. | Workbook structure: Kristiansand Alarm JSON Review v3. Style: Renasys Ignition presentation, 8 October 2026.

## Alarm list
Aqua Rig alarm list | Aqua Rig alarm list | Aqua Rig alarm list | Aqua Rig alarm list | Aqua Rig alarm list | Aqua Rig alarm list | Aqua Rig alarm list | Aqua Rig alarm list | Aqua Rig alarm list
AR-V1-01-RE26 - All alarm flags and diagnostic fields | AR-V1-01-RE26 - All alarm flags and diagnostic fields | AR-V1-01-RE26 - All alarm flags and diagnostic fields | AR-V1-01-RE26 - All alarm flags and diagnostic fields | AR-V1-01-RE26 - All alarm flags and diagnostic fields | AR-V1-01-RE26 - All alarm flags and diagnostic fields | AR-V1-01-RE26 - All alarm flags and diagnostic fields | AR-V1-01-RE26 - All alarm flags and diagnostic fields | AR-V1-01-RE26 - All alarm flags and diagnostic fields
Notify values are proposals for external notifications. HMI Enabled is shown separately. | Notify values are proposals for external notifications. HMI Enabled is shown separately. | Notify values are proposals for external notifications. HMI Enabled is shown separately. | Notify values are proposals for external notifications. HMI Enabled is shown separately. | No Aqua Rig notification JSON supplied. All routing values require review. | No Aqua Rig notification JSON supplied. All routing values require review. | No Aqua Rig notification JSON supplied. All routing values require review. | No Aqua Rig notification JSON supplied. All routing values require review. | No Aqua Rig notification JSON supplied. All routing values require review.
Listed tags | 109 | Proposed notify | 44 | Proposed no_notify | 65 | Undecided | 0
Notify: editable TRUE/FALSE. HMI Enabled: current XML setting; n.a. indicates a diagnostic companion, not an independent alarm. | Notify: editable TRUE/FALSE. HMI Enabled: current XML setting; n.a. indicates a diagnostic companion, not an independent alarm. | Notify: editable TRUE/FALSE. HMI Enabled: current XML setting; n.a. indicates a diagnostic companion, not an independent alarm. | Notify: editable TRUE/FALSE. HMI Enabled: current XML setting; n.a. indicates a diagnostic companion, not an independent alarm. | Notify: editable TRUE/FALSE. HMI Enabled: current XML setting; n.a. indicates a diagnostic companion, not an independent alarm. | Notify: editable TRUE/FALSE. HMI Enabled: current XML setting; n.a. indicates a diagnostic companion, not an independent alarm. | Notify: editable TRUE/FALSE. HMI Enabled: current XML setting; n.a. indicates a diagnostic companion, not an independent alarm. | Notify: editable TRUE/FALSE. HMI Enabled: current XML setting; n.a. indicates a diagnostic companion, not an independent alarm. | Notify: editable TRUE/FALSE. HMI Enabled: current XML setting; n.a. indicates a diagnostic companion, not an independent alarm.
Tag | Notify | Type | Description | Routing status | OPC UA type | Notes / action | HMI Enabled | HMI source path
TestAlarm | TRUE | ALARM | Test alarm - Test alarm signal | PROPOSED notify | BOOL | Test signal. Confirm external notification routing. | TRUE | HMI_COM_OPC/Alarms/TestAlarm
M1_WaterFlushingSM_ColdValve_Fault | TRUE | FAULT | POV121 - Water flushing - Cold Valve - [!HMI_COM_OPC/Alarms/M1_WaterFlushingSM_ColdValve_FaultStatus] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_WaterFlushingSM_ColdValve_Fault
M1_WaterFlushingSM_WarmValve_Fault | TRUE | FAULT | POV122 - Water flushing - Warm Valve - [!HMI_COM_OPC/Alarms/M1_WaterFlushingSM_WarmValve_FaultStatus] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_WaterFlushingSM_WarmValve_Fault
M1_WaterFlushingSM_PumpSelectionValve_Fault | TRUE | FAULT | POV123 - Water flushing - Pump selection valve fault - [!HMI_COM_OPC/Alarms/M1_WaterFlushingSM_PumpSelectionValve_FaultStatus] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_WaterFlushingSM_PumpSelectionValve_Fault
M1_DrumMotor_SBE_YF | TRUE | FAULT | M101 - Drum motor - SBE Fault - [!HMI_COM_OPC/Alarms/M1_DrumMotor_SBE_YFS] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_DrumMotor_SBE_YF
M1_DrumMotor_OA_YF | TRUE | FAULT | M101 - Drum motor - Output function Fault - [!HMI_COM_OPC/Alarms/M1_DrumMotor_OA_YFS] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_DrumMotor_OA_YF
M1_DrumMotor_OA_WV | TRUE | ALARM | M101 - Drum motor - Output deviation warning | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_DrumMotor_OA_WV
M1_HybridPump_OutletValve_Fault | TRUE | FAULT | POV111 - Hybrid pump - Outlet valve fault - [!HMI_COM_OPC/Alarms/M1_HybridPump_OutletValve_FaultStatus] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_HybridPump_OutletValve_Fault
M1_HybridPump_SBE_YF | TRUE | FAULT | P111 - Inlet / hybrid pump - SBE Fault - [!HMI_COM_OPC/Alarms/M1_HybridPump_SBE_YFS] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_HybridPump_SBE_YF
M1_HybridPump_OA_YF | TRUE | FAULT | P111 - Inlet / hybrid pump - Output function Fault - [!HMI_COM_OPC/Alarms/M1_HybridPump_OA_YFS] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_HybridPump_OA_YF
M1_HybridPump_OA_WV | TRUE | ALARM | P111 - Inlet / hybrid pump - Output deviation warning | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_HybridPump_OA_WV
M1_HighPressurePump_LossFreshWater | TRUE | FAULT | P121 - High pressure pump (HPP) - Loss of freshwater | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_HighPressurePump_LossFreshWater
M1_HighPressurePump_SBE_YF | TRUE | FAULT | P121 - High pressure pump (HPP) - SBE Fault - [!HMI_COM_OPC/Alarms/M1_HighPressurePump_SBE_YFS] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_HighPressurePump_SBE_YF
M1_HighPressurePump_OA_YF | TRUE | FAULT | P121 - High pressure pump (HPP) - Output function Fault - [!HMI_COM_OPC/Alarms/M1_HighPressurePump_OA_YFS] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_HighPressurePump_OA_YF
M1_HighPressurePump_OA_WV | TRUE | ALARM | P121 - High pressure pump (HPP) - Output deviation warning | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_HighPressurePump_OA_WV
M1_PressureIncreasingPump_LossFreshWater | TRUE | FAULT | P122 - Pressure increasing pump (PIP) - Loss of freshwater | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_PressureIncreasingPump_LossFreshWater
M1_PressureIncreasingPump_SBE_YF | TRUE | FAULT | P122 - Pressure increasing pump (PIP) - SBE Fault - [!HMI_COM_OPC/Alarms/M1_PressureIncreasingPump_SBE_YFS] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_PressureIncreasingPump_SBE_YF
M1_PressureIncreasingPump_OA_YF | TRUE | FAULT | P122 - Pressure increasing pump (PIP) - Output function Fault - [!HMI_COM_OPC/Alarms/M1_PressureIncreasingPump_OA_YFS] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_PressureIncreasingPump_OA_YF
M1_PressureIncreasingPump_OA_WV | TRUE | ALARM | P122 - Pressure increasing pump (PIP) - Output deviation warning | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_PressureIncreasingPump_OA_WV
M1_Airknife_LowPressure | TRUE | FAULT | FRL151 - Airknife - Low Pressure | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/M1_Airknife_LowPressure
VFD111_YF | TRUE | FAULT | P111 - Inlet / hybrid pump - Speed feedback - Signal Fault | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/VFD111_YF
VFD111_AHH | FALSE | ALARM | P111 - Inlet / hybrid pump - Speed feedback - Limit - HH, value: [!HMI_COM_OPC/OS_OUT/VFD111_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD111_AHH
VFD111_WH | FALSE | ALARM | P111 - Inlet / hybrid pump - Speed feedback - Warning - H, value: [!HMI_COM_OPC/OS_OUT/VFD111_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD111_WH
VFD111_WL | FALSE | ALARM | P111 - Inlet / hybrid pump - Speed feedback - Warning - L, value: [!HMI_COM_OPC/OS_OUT/VFD111_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD111_WL
VFD111_ALL | FALSE | ALARM | P111 - Inlet / hybrid pump - Speed feedback - Limit - LL, value: [!HMI_COM_OPC/OS_OUT/VFD111_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD111_ALL
VFD121_YF | TRUE | FAULT | P121 - High pressure pump (HPP) - Speed feedback - Signal Fault | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/VFD121_YF
VFD121_AHH | FALSE | ALARM | P121 - High pressure pump (HPP) - Speed feedback - Limit - HH, value: [!HMI_COM_OPC/OS_OUT/VFD121_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD121_AHH
VFD121_WH | FALSE | ALARM | P121 - High pressure pump (HPP) - Speed feedback - Warning - H, value: [!HMI_COM_OPC/OS_OUT/VFD121_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD121_WH
VFD121_WL | FALSE | ALARM | P121 - High pressure pump (HPP) - Speed feedback - Warning - L, value: [!HMI_COM_OPC/OS_OUT/VFD121_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD121_WL
VFD121_ALL | FALSE | ALARM | P121 - High pressure pump (HPP) - Speed feedback - Limit - LL, value: [!HMI_COM_OPC/OS_OUT/VFD121_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD121_ALL
VFD122_YF | TRUE | FAULT | P122 - Pressure increasing pump (PIP) - Speed feedback - Signal Fault | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/VFD122_YF
VFD122_AHH | FALSE | ALARM | P122 - Pressure increasing pump (PIP) - Speed feedback - Limit - HH, value: [!HMI_COM_OPC/OS_OUT/VFD122_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD122_AHH
VFD122_WH | FALSE | ALARM | P122 - Pressure increasing pump (PIP) - Speed feedback - Warning - H, value: [!HMI_COM_OPC/OS_OUT/VFD122_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD122_WH
VFD122_WL | FALSE | ALARM | P122 - Pressure increasing pump (PIP) - Speed feedback - Warning - L, value: [!HMI_COM_OPC/OS_OUT/VFD122_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD122_WL
VFD122_ALL | FALSE | ALARM | P122 - Pressure increasing pump (PIP) - Speed feedback - Limit - LL, value: [!HMI_COM_OPC/OS_OUT/VFD122_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD122_ALL
VFD101_YF | TRUE | FAULT | M101 - Drum filter - Speed feedback - Signal Fault | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/VFD101_YF
VFD101_AHH | FALSE | ALARM | M101 - Drum filter - Speed feedback - Limit - HH, value: [!HMI_COM_OPC/OS_OUT/VFD101_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD101_AHH
VFD101_WH | FALSE | ALARM | M101 - Drum filter - Speed feedback - Warning - H, value: [!HMI_COM_OPC/OS_OUT/VFD101_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD101_WH
VFD101_WL | FALSE | ALARM | M101 - Drum filter - Speed feedback - Warning - L, value: [!HMI_COM_OPC/OS_OUT/VFD101_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD101_WL
VFD101_ALL | FALSE | ALARM | M101 - Drum filter - Speed feedback - Limit - LL, value: [!HMI_COM_OPC/OS_OUT/VFD101_Y] | PROPOSED no_notify | BOOL | Disabled: only VFD YF is enabled. | FALSE | HMI_COM_OPC/Alarms/VFD101_ALL
FRL151_YF | TRUE | FAULT | FRL151 - Airknive FRL - Fault | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/FRL151_YF
FRL151_AHH | FALSE | ALARM | FRL151 - Airknive FRL - Limit - HH, value: [!HMI_COM_OPC/OS_OUT/FRL151_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/FRL151_AHH
FRL151_WH | FALSE | ALARM | FRL151 - Airknive FRL - Warning - H, value: [!HMI_COM_OPC/OS_OUT/FRL151_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/FRL151_WH
FRL151_WL | FALSE | ALARM | FRL151 - Airknive FRL - Warning - L, value: [!HMI_COM_OPC/OS_OUT/FRL151_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/FRL151_WL
FRL151_ALL | FALSE | ALARM | FRL151 - Airknive FRL - Limit - LL, value: [!HMI_COM_OPC/OS_OUT/FRL151_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/FRL151_ALL
FT111_YF | TRUE | FAULT | FT111 - Flowmeter - Fault | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/FT111_YF
FT111_AHH | FALSE | ALARM | FT111 - Flowmeter - Limit - HH, value: [!HMI_COM_OPC/OS_OUT/FT111_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/FT111_AHH
FT111_WH | FALSE | ALARM | FT111 - Flowmeter - Warning - H, value: [!HMI_COM_OPC/OS_OUT/FT111_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/FT111_WH
FT111_WL | FALSE | ALARM | FT111 - Flowmeter - Warning - L, value: [!HMI_COM_OPC/OS_OUT/FT111_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/FT111_WL
FT111_ALL | FALSE | ALARM | FT111 - Flowmeter - Limit - LL, value: [!HMI_COM_OPC/OS_OUT/FT111_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/FT111_ALL
LT111_YF | TRUE | FAULT | LT111 - Drum filter - Leveltransmitter - Fault | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/LT111_YF
LT111_AHH | TRUE | ALARM | LT111 - Drum filter - Limit - HH, value: [!HMI_COM_OPC/OS_OUT/LT111_Y] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/LT111_AHH
LT111_WH | FALSE | ALARM | LT111 - Drum filter - Warning - H, value: [!HMI_COM_OPC/OS_OUT/LT111_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/LT111_WH
LT111_WL | FALSE | ALARM | LT111 - Drum filter - Warning - L, value: [!HMI_COM_OPC/OS_OUT/LT111_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/LT111_WL
LT111_ALL | FALSE | ALARM | LT111 - Drum filter - Limit - LL, value: [!HMI_COM_OPC/OS_OUT/LT111_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/LT111_ALL
PT151_YF | TRUE | FAULT | PT151 - Instrument air - Pressuretransmitter - Fault | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/PT151_YF
PT151_AHH | FALSE | ALARM | PT151 - Instrument air - Limit - HH, value: [!HMI_COM_OPC/OS_OUT/PT151_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/PT151_AHH
PT151_WH | FALSE | ALARM | PT151 - Instrument air - Warning - H, value: [!HMI_COM_OPC/OS_OUT/PT151_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/PT151_WH
PT151_WL | TRUE | ALARM | PT151 - Instrument air - Warning - L, value: [!HMI_COM_OPC/OS_OUT/PT151_Y] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/PT151_WL
PT151_ALL | TRUE | ALARM | PT151 - Instrument air - Limit - LL, value: [!HMI_COM_OPC/OS_OUT/PT151_Y] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/PT151_ALL
PT121_YF | TRUE | FAULT | PT121 - Pressure transmitter - Main water supply - Fault | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/PT121_YF
PT121_AHH | FALSE | ALARM | PT121 - Pressure transmitter - Limit - HH - Main water supply, value: [!HMI_COM_OPC/OS_OUT/PT121_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/PT121_AHH
PT121_WH | FALSE | ALARM | PT121 - Pressure transmitter - Warning - H - Main water supply, value: [!HMI_COM_OPC/OS_OUT/PT121_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/PT121_WH
PT121_WL | TRUE | ALARM | PT121 - Pressure transmitter - Warning - L - Main water supply, value: [!HMI_COM_OPC/OS_OUT/PT121_Y] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/PT121_WL
PT121_ALL | TRUE | ALARM | PT121 - Pressure transmitter - Limit - LL - Main water supply, value: [!HMI_COM_OPC/OS_OUT/PT121_Y] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/PT121_ALL
PT122_YF | TRUE | FAULT | PT122 - High pressure pump (HPP) - Pressuretransmitter - Fault | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/PT122_YF
PT122_AHH | FALSE | ALARM | PT122 - High pressure pump (HPP) - Limit - HH, value: [!HMI_COM_OPC/OS_OUT/PT122_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/PT122_AHH
PT122_WH | TRUE | ALARM | PT122 - High pressure pump (HPP) - Warning - H, value: [!HMI_COM_OPC/OS_OUT/PT122_Y] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/PT122_WH
PT122_WL | FALSE | ALARM | PT122 - High pressure pump (HPP) - Warning - L, value: [!HMI_COM_OPC/OS_OUT/PT122_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/PT122_WL
PT122_ALL | FALSE | ALARM | PT122 - High pressure pump (HPP) - Limit - LL, value: [!HMI_COM_OPC/OS_OUT/PT122_Y] | PROPOSED no_notify | BOOL | Disabled in the agreed HMI alarm configuration. | FALSE | HMI_COM_OPC/Alarms/PT122_ALL
PT123_YF | TRUE | FAULT | PT123 - Pressure increasing pump (PIP) - Pressuretransmitter - Fault | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/PT123_YF
PT123_AHH | FALSE | ALARM | PT123 - Pressure increasing pump (PIP) - Limit - HH, value: [!HMI_COM_OPC/OS_OUT/PT123_Y] | PROPOSED no_notify | BOOL | Enabled state matches PT122. | FALSE | HMI_COM_OPC/Alarms/PT123_AHH
PT123_WH | TRUE | ALARM | PT123 - Pressure increasing pump (PIP) - Warning - H, value: [!HMI_COM_OPC/OS_OUT/PT123_Y] | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/PT123_WH
PT123_WL | FALSE | ALARM | PT123 - Pressure increasing pump (PIP) - Warning - L, value: [!HMI_COM_OPC/OS_OUT/PT123_Y] | PROPOSED no_notify | BOOL | Enabled state matches PT122. | FALSE | HMI_COM_OPC/Alarms/PT123_WL
PT123_ALL | FALSE | ALARM | PT123 - Pressure increasing pump (PIP) - Limit - LL, value: [!HMI_COM_OPC/OS_OUT/PT123_Y] | PROPOSED no_notify | BOOL | Enabled state matches PT122. | FALSE | HMI_COM_OPC/Alarms/PT123_ALL
PT191_YF | TRUE | FAULT | PT191 - Inlet tank - Pressuretransmitter - Fault | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/PT191_YF
PT191_AHH | FALSE | ALARM | PT191 - Inlet tank - Limit - HH, value: [!HMI_COM_OPC/OS_OUT/PT191_Y] | PROPOSED no_notify | BOOL | Disabled: only PT191_YF is enabled. | FALSE | HMI_COM_OPC/Alarms/PT191_AHH
PT191_WH | FALSE | ALARM | PT191 - Inlet tank - Limit - WH, value: [!HMI_COM_OPC/OS_OUT/PT191_Y] | PROPOSED no_notify | BOOL | Disabled: only PT191_YF is enabled. | FALSE | HMI_COM_OPC/Alarms/PT191_WH
PT191_WL | FALSE | ALARM | PT191 - Inlet tank - Warning - L, value: [!HMI_COM_OPC/OS_OUT/PT191_Y] | PROPOSED no_notify | BOOL | Disabled: only PT191_YF is enabled. | FALSE | HMI_COM_OPC/Alarms/PT191_WL
PT191_ALL | FALSE | ALARM | PT191 - Inlet tank - Limit - LL, value: [!HMI_COM_OPC/OS_OUT/PT191_Y] | PROPOSED no_notify | BOOL | Disabled: only PT191_YF is enabled. | FALSE | HMI_COM_OPC/Alarms/PT191_ALL
VFD111_F_Y | FALSE | FAULT | P111 - Inlet / hybrid pump - VFD fault | PROPOSED no_notify | BOOL | Disabled: represented through the SBE alarm. | FALSE | HMI_COM_OPC/Alarms/VFD111_F_Y
VFD121_F_Y | FALSE | FAULT | P121 - High pressure pump (HPP) - VFD | PROPOSED no_notify | BOOL | Disabled: represented through the SBE alarm. | FALSE | HMI_COM_OPC/Alarms/VFD121_F_Y
VFD122_F_Y | FALSE | FAULT | P122 - Pressure increasing pump (PIP) - VFD fault | PROPOSED no_notify | BOOL | Disabled: represented through the SBE alarm. | FALSE | HMI_COM_OPC/Alarms/VFD122_F_Y
VFD101_F_Y | FALSE | FAULT | M101 - Drum filter - VFD | PROPOSED no_notify | BOOL | Disabled: represented through the SBE alarm. | FALSE | HMI_COM_OPC/Alarms/VFD101_F_Y
KC151_F_Y | TRUE | FAULT | KC151 - Compressor fault | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/KC151_F_Y
Q102_Y | TRUE | FAULT | Q102 - Tripped fuse - Compressor | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/Q102_Y
Q103_Y | TRUE | FAULT | Q103 - Tripped fuse - Water heater | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/Q103_Y
ESR001_Y | TRUE | ALARM | ESR001 - EM-stop activated | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/ESR001_Y
ECB101_Y | TRUE | FAULT | ECB101 - Tripped DC fuse - Electronic circuit breaker | PROPOSED notify | BOOL |  | TRUE | HMI_COM_OPC/Alarms/ECB101_Y
M1_DrumMotor_OA_YFI | FALSE | FAULT | M101 - Drum motor - Output function Fault - Fault code | PROPOSED no_notify | INT | Diagnostic companion to M1_DrumMotor_OA_YF. Fault code; no independent alarm trigger. | n.a. | HMI_COM_OPC/Alarms/M1_DrumMotor_OA_YFI
M1_DrumMotor_OA_YFS | FALSE | FAULT | M101 - Drum motor - Output function Fault - Fault description | PROPOSED no_notify | STRING | Diagnostic companion to M1_DrumMotor_OA_YF. Text captured in the parent alarm message. | n.a. | HMI_COM_OPC/Alarms/M1_DrumMotor_OA_YFS
M1_DrumMotor_SBE_YFI | FALSE | FAULT | M101 - Drum motor - SBE Fault - Fault code | PROPOSED no_notify | INT | Diagnostic companion to M1_DrumMotor_SBE_YF. Fault code; no independent alarm trigger. | n.a. | HMI_COM_OPC/Alarms/M1_DrumMotor_SBE_YFI
M1_DrumMotor_SBE_YFS | FALSE | FAULT | M101 - Drum motor - SBE Fault - Fault description | PROPOSED no_notify | STRING | Diagnostic companion to M1_DrumMotor_SBE_YF. Text captured in the parent alarm message. | n.a. | HMI_COM_OPC/Alarms/M1_DrumMotor_SBE_YFS
M1_HighPressurePump_OA_YFI | FALSE | FAULT | P121 - High pressure pump (HPP) - Output function Fault - Fault code | PROPOSED no_notify | INT | Diagnostic companion to M1_HighPressurePump_OA_YF. Fault code; no independent alarm trigger. | n.a. | HMI_COM_OPC/Alarms/M1_HighPressurePump_OA_YFI
M1_HighPressurePump_OA_YFS | FALSE | FAULT | P121 - High pressure pump (HPP) - Output function Fault - Fault description | PROPOSED no_notify | STRING | Diagnostic companion to M1_HighPressurePump_OA_YF. Text captured in the parent alarm message. | n.a. | HMI_COM_OPC/Alarms/M1_HighPressurePump_OA_YFS
M1_HighPressurePump_SBE_YFI | FALSE | FAULT | P121 - High pressure pump (HPP) - SBE Fault - Fault code | PROPOSED no_notify | INT | Diagnostic companion to M1_HighPressurePump_SBE_YF. Fault code; no independent alarm trigger. | n.a. | HMI_COM_OPC/Alarms/M1_HighPressurePump_SBE_YFI
M1_HighPressurePump_SBE_YFS | FALSE | FAULT | P121 - High pressure pump (HPP) - SBE Fault - Fault description | PROPOSED no_notify | STRING | Diagnostic companion to M1_HighPressurePump_SBE_YF. Text captured in the parent alarm message. | n.a. | HMI_COM_OPC/Alarms/M1_HighPressurePump_SBE_YFS
M1_HybridPump_OA_YFI | FALSE | FAULT | P111 - Inlet / hybrid pump - Output function Fault - Fault code | PROPOSED no_notify | INT | Diagnostic companion to M1_HybridPump_OA_YF. Fault code; no independent alarm trigger. | n.a. | HMI_COM_OPC/Alarms/M1_HybridPump_OA_YFI
M1_HybridPump_OA_YFS | FALSE | FAULT | P111 - Inlet / hybrid pump - Output function Fault - Fault description | PROPOSED no_notify | STRING | Diagnostic companion to M1_HybridPump_OA_YF. Text captured in the parent alarm message. | n.a. | HMI_COM_OPC/Alarms/M1_HybridPump_OA_YFS
M1_HybridPump_OutletValve_FaultStatus | FALSE | FAULT | POV111 - Hybrid pump - Outlet valve fault - Fault description | PROPOSED no_notify | STRING(40) | Diagnostic companion to M1_HybridPump_OutletValve_Fault. Text captured in the parent alarm message. | n.a. | HMI_COM_OPC/Alarms/M1_HybridPump_OutletValve_FaultStatus
M1_HybridPump_SBE_YFI | FALSE | FAULT | P111 - Inlet / hybrid pump - SBE Fault - Fault code | PROPOSED no_notify | INT | Diagnostic companion to M1_HybridPump_SBE_YF. Fault code; no independent alarm trigger. | n.a. | HMI_COM_OPC/Alarms/M1_HybridPump_SBE_YFI
M1_HybridPump_SBE_YFS | FALSE | FAULT | P111 - Inlet / hybrid pump - SBE Fault - Fault description | PROPOSED no_notify | STRING | Diagnostic companion to M1_HybridPump_SBE_YF. Text captured in the parent alarm message. | n.a. | HMI_COM_OPC/Alarms/M1_HybridPump_SBE_YFS
M1_PressureIncreasingPump_OA_YFI | FALSE | FAULT | P122 - Pressure increasing pump (PIP) - Output function Fault - Fault code | PROPOSED no_notify | INT | Diagnostic companion to M1_PressureIncreasingPump_OA_YF. Fault code; no independent alarm trigger. | n.a. | HMI_COM_OPC/Alarms/M1_PressureIncreasingPump_OA_YFI
M1_PressureIncreasingPump_OA_YFS | FALSE | FAULT | P122 - Pressure increasing pump (PIP) - Output function Fault - Fault description | PROPOSED no_notify | STRING | Diagnostic companion to M1_PressureIncreasingPump_OA_YF. Text captured in the parent alarm message. | n.a. | HMI_COM_OPC/Alarms/M1_PressureIncreasingPump_OA_YFS
M1_PressureIncreasingPump_SBE_YFI | FALSE | FAULT | P122 - Pressure increasing pump (PIP) - SBE Fault - Fault code | PROPOSED no_notify | INT | Diagnostic companion to M1_PressureIncreasingPump_SBE_YF. Fault code; no independent alarm trigger. | n.a. | HMI_COM_OPC/Alarms/M1_PressureIncreasingPump_SBE_YFI
M1_PressureIncreasingPump_SBE_YFS | FALSE | FAULT | P122 - Pressure increasing pump (PIP) - SBE Fault - Fault description | PROPOSED no_notify | STRING | Diagnostic companion to M1_PressureIncreasingPump_SBE_YF. Text captured in the parent alarm message. | n.a. | HMI_COM_OPC/Alarms/M1_PressureIncreasingPump_SBE_YFS
M1_WaterFlushingSM_ColdValve_FaultStatus | FALSE | FAULT | POV121 - Water flushing - Cold Valve - Fault description | PROPOSED no_notify | STRING(40) | Diagnostic companion to M1_WaterFlushingSM_ColdValve_Fault. Text captured in the parent alarm message. | n.a. | HMI_COM_OPC/Alarms/M1_WaterFlushingSM_ColdValve_FaultStatus
M1_WaterFlushingSM_PumpSelectionValve_FaultStatus | FALSE | FAULT | POV123 - Water flushing - Pump selection valve fault - Fault description | PROPOSED no_notify | STRING(40) | Diagnostic companion to M1_WaterFlushingSM_PumpSelectionValve_Fault. Text captured in the parent alarm message. | n.a. | HMI_COM_OPC/Alarms/M1_WaterFlushingSM_PumpSelectionValve_FaultStatus
M1_WaterFlushingSM_WarmValve_FaultStatus | FALSE | FAULT | POV122 - Water flushing - Warm Valve - Fault description | PROPOSED no_notify | STRING(40) | Diagnostic companion to M1_WaterFlushingSM_WarmValve_Fault. Text captured in the parent alarm message. | n.a. | HMI_COM_OPC/Alarms/M1_WaterFlushingSM_WarmValve_FaultStatus